## Section X1
SECTION X1: PRELIMINARY AND GENERAL
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL AND LABOUR
[5 empty] | RATE | TOTAL
[5 empty] | N$ | N$
1 |  | PRELIMINARY AND GENERAL
1.1 |  | GENERAL
1.1.1 |  | Establishment of Site | Item | 1 |  | 0
1.1.2 |  | Monthly site meeting attendance | Item | 1 |  | 0
1.1.3 |  | All overheads and complied will all Prelimininary, General and Special Condition of Contract and Labour Relations not included specifically in this Schedule of Quantities | Item | 1 |  | 0
1.1.4 |  | Allowance for AS-Built drawings and documentations | Item | 1 |  | 0
1.1.5 |  | Allowance for 12 months guarantee period | Item | 1
1.2 |  | TRANSPORT
1.2.1 |  | Allowance for transport of all material and equipment to site | Item | 1 |  | 0
1.3 |  | STORAGE
1.3.1 |  | Storage facility for all plant, material and equipment, including protection and safeguarding | Item | 1 |  | 0
1.4 |  | PERMITS AND NOTICES
1.4.1 |  | Obtaining all necessary permits, and issuing of all required notices | Item | 1 |  | 0
1.5 |  | CO-ORDINATION ON SITE |  | 1 |  | 0
1.5.1 |  | C-ordination and co-operation on site with all other organisations and/or contractors | Item | 1 |  | 0
1.6 |  | COMMISSIONING AND TESTING |  | 1 |  | 0
1.6.1 |  | Commissioning and accepatnce test of all equipment and material as specified or implied in the specification | Item | 1 |  | 0
1.7 |  | INSURANCE
1.7.1 |  | Insurance allowance as specified under the conditions
TOTALS CARRIED FORWARD TO NEXT PAGE | [5 empty] | 0
SECTION X1: PRELIMINARY AND GENERAL
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL AND LABOUR
[5 empty] | RATE | TOTAL
[5 empty] | N$ | N$
TOTALS BROUGHT FORWARD FROM PREVIOUS PAGE | [5 empty] | 0
1.8 |  | ALL OTHER PRELIMINARY NOT LISTED
1.8.1 |  | Items as per the conditions of contract, Premeambles and Technical Specifications and not contained in any of the above items
1.8.2 |  |  | Item | 1 |  | 0
1.8.3 |  |  | Item | 1 |  | 0
1.8.4 |  |  | Item | 1 |  | 0
1.8.5 |  |  | Item | 1 |  | 0
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0

## Section X2
SECTION X2:ELECTRICAL INSTALLATION: LV CABLES AND TERMINATIONS
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
2 |  | LV CABLES AND TERMINATIONS
2.1 |  | 600/1000V PVC/PVC/SWA/PVC Cu CABLES
2.1.1 |  | 2C x16mm² | m | 80 |  | 0 |  | 0
2.1.2 |  | 2C x 16mm² Termination | No. | 2 |  | 0 |  | 0
2.1.3 |  | 2C x 10mm² | m | 500 |  | 0 |  | 0
2.1.4 |  | 2C x 10mm² Termination | No. | 26 |  | 0 |  | 0
2.2 |  | Bare copper earth wire (BCEW) installed in various ways with cables including terminations | [5 empty] | 0
2.2.1 |  | 10mm² | m | 80
2.1.2 |  | 10mm² Termination | No. | 2
2.2.3 |  | 6mm² | m | 500 |  | 0 |  | 0
2.1.4 |  | 6mm² Termination | No. | 26 |  | 0
2.3 |  | WARNING TAPE |  |  |  | 0 |  | 0
2.3.1 |  | Yellow Warning Tape installed 200mm above cables | m | 600 |  | 0 |  | 0
2.4 |  | Any other items necessary to complete the above LV Cables not listed elsewhere | [5 empty] | 0
Specify:
[6 empty] | 0 |  | 0
0
0
0
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 |  | 0

## Section X3
SECTION X3: TRENCHES,SLEEVE PIPES AND MANHOLES
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
3 |  | TRENCHES,SLEEVE PIPES AND MANHOLES
3.1 |  | Cable & Sleevepipe Trenches Trenching, backfilling and compaction for cable and uPVC pipe installations as specified including removal, storing and replacing of interlock paving and road kerbstones (allow for replacement of breakages). Rates to include trench sidewall stabilization and traffic safety fencing during installation works.
3.1.1 |  | Cable Trench 350 mm wide x 750 mm deep in earth .(SANS 1200 DA,paragraph 3.1.2.(a)) | m | 50 |  | 0 |  | 0
3.1.2 |  | Cable Trench 350 mm wide x 750 mm deep in soft rock . (SANS 1200 DA,paragraph 3.1.2.(b)) | m | 50 |  | 0 |  | 0
3.1.3 |  | Cable Trench 350 mm wide x 750 mm deep in hard rock (SANS 1200 DA,paragraph 3.1.2.(c)) | m | 650 |  | 0 |  | 0
3.2 |  | Sleeve Pipes & Bends uPVC sleeve pipes complete installed in trench or within or below concrete slabs
3.2.1 |  | ø 50 mm Sleeve Pipe | m | 24 |  | 0 |  | 0
3.2.2 |  | ø 50mm x 90˚ soft bend | No. | 2
3.2.3 |  | ø 75mm Sleeve Pipe | m | 24
3.2.4 |  | ø 75 mm x 90˚ soft bend | No. | 2
3.3 |  | Any other items necessary to complete the above TRENCHES,SLEEVE PIPES AND MANHOLES not listed elsewhere
Specify:
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 |  | 0

## Section X4
SECTION X4: ELECTRICAL INSTALLATION: LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
4 |  | LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR
As per standard and project specifications and according to wiring diagrams. Enclosure rates to include housing, busbars neutral bars, earth bars, busbar links, mounting plates, trays, architraves, doors or transparent covers with hinges as well as all fittings and fixtures for a complete distribution board installation and commissioning excluding switchgear (listed separately below). All boards to be sized for 35% switchgear spare capacity.All switchgear except to be suitable for DIN-rail mounting.
4.1 |  | MDB:SCHOOL
0
4.1.1 |  | Weatherproof Surface wall-mounted enclosure, Epoxy powder coated, and have top-hung doors with pad-lockable latches, equal to the GEM Manufacture | No | 1 |  | 0 |  | 0
4.1.2 |  | Switchgear for the above, installed, wired , connected
4.1.2.1 |  | 50A SP MCB | No | 1 |  | 0 |  | 0
4.1.2.2 |  | 30A SP MCB | No | 5 |  | 0 |  | 0
4.1.2.3 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.1.2.4 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.1.2.5 |  | 63A DP ELCB | No | 1 |  | 0 |  | 0
4.2 |  | DB-1:ABLUTION (EXISTING)
4.2.1 |  | Switchgear for the above, installed, wired , connected | [5 empty] | 0
4.2.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.2.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.2.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.3 |  | DB-2:STAFF OFFICE (EXISTING)
0
4.3.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.3.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.3.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.3.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
TOTALS CARRIED FORWARD TO NEXT PAGE | [5 empty] | 0 |  | 0
SECTION X4: ELECTRICAL INSTALLATION: LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
TOTALS BROUGHT FORWARD FROM PREVIOUS PAGE | [5 empty] | 0 |  | 0
4.4 |  | DB-3:BLOCK 3 (EXISTING)
0
4.4.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.4.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.4 |  | DB-3.1:HOSTEL 4 (EXISTING)
0
4.4.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.4.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.4 |  | DB-3.2:HOSTEL 5 (EXISTING)
0
4.4.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.4.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.4 |  | DB-4:HOSTEL 1 (EXISTING)
0
4.4.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.4.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.4.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
TOTALS CARRIED FORWARD TO NEXT PAGE | [5 empty] | 0 |  | 0
SECTION X4: ELECTRICAL INSTALLATION: LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
TOTALS BROUGHT FORWARD FROM PREVIOUS PAGE | [5 empty] | 0 |  | 0
4.5 |  | DB-4.1:HOSTEL 2 (EXISTING)
0
4.5.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.5.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.5.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.5.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.6 |  | DB-4.2:KITCHEN (NEW)
0
4.6.1 |  | Weatherproof Surface wall-mounted enclosure, Epoxy powder coated, and have top-hung doors with pad-lockable latches, equal to the GEM Manufacture | No | 1 |  | 0 |  | 0
4.6.2 |  | Switchgear for the above, installed, wired , connected
4.6.2.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.6.2.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.6.2.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
[6 empty] | 0 |  | 0
4.6.2.4 |  | 63A DP ELCB | No | 1 |  | 0 |  | 0
4.7 |  | DB-4.3:HOSTEL 3 (EXISTING)
0
4.7.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.7.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.7.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.7.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.8 |  | DB-5:BLOCK 2 (EXISTING)
0
4.8.1 |  | Switchgear for the above, installed, wired , connected |  |  |  | 0 |  | 0
4.8.1.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.8.1.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.8.1.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
TOTALS CARRIED FORWARD TO NEXT PAGE | [5 empty] | 0 |  | 0
SECTION X4: ELECTRICAL INSTALLATION: LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
TOTALS BROUGHT FORWARD FROM PREVIOUS PAGE | [5 empty] | 0 |  | 0
4.9 |  | DB-H1:HOUSE 1(NEW)
0
4.9.1 |  | Weatherproof Surface wall-mounted enclosure, Epoxy powder coated, and have top-hung doors with pad-lockable latches, equal to the GEM Manufacture | No | 1 |  | 0 |  | 0
4.9.2 |  | Switchgear for the above, installed, wired , connected
0
4.9.2.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.9.2.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.9.2.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
4.9.2.4 |  | 63A DP ELCB | No | 1
4.1 |  | DB-H2:HOUSE 2(NEW)
0
4.10.1 |  | Weatherproof Surface wall-mounted enclosure, Epoxy powder coated, and have top-hung doors with pad-lockable latches, equal to the GEM Manufacture | No | 1 |  | 0 |  | 0
4.10.2 |  | Switchgear for the above, installed, wired , connected
4.10.2.1 |  | 30A SP MCB | No | 1 |  | 0 |  | 0
4.10.2.2 |  | 20A SP MCB | No | 1 |  | 0 |  | 0
4.10.2.3 |  | 10A SP MCB | No | 1 |  | 0 |  | 0
0
4.10.2.4 |  | 63A DP ELCB | No | 1 |  | 0 |  | 0
4.11 |  | Earthing of main distibution boards with 16sqmm green PVC insulated copper conductor terminating on a 1.2m long 16mm dia. solid steel copper bonded earth spike burried 1.5m below ground level. | No. | 2
4.12 |  | Any other items necessary to complete the above DB and Switchegear Installations not listed elsewhere
Specify:
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 |  | 0

## Section X5
SECTION X5: ELECTRICAL INSTALLATION:OUTLETS AS SPECIFIED
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
5 |  | OUTLETS AS SPECIFIED
5.1 |  | Switched socket outlet "Mains Power" flush wall mounted single type. Supply, delivery, and installation of single switched socket outlet for 16A - 3 Pin/230V South African Standard plugs type Legrand Arteor Colour White. The rate shall include all conduiting, ducting, and wiring from the DB. 2.5mm² PVC insulated copper wire shall be used for live and neutral conductors, and 2,5 mm² PVC insulated copper wire shall be used for the earth conductor. The socket shall be installed inside a flush-mounted 100 x 100 mm PVC box. Note: Each Socket-outlet point shall include socket outlets complying with the dimensions of SANS 164-1 in addition to the SANS 164-2 socket-outlet. | No | 20 |  | 0 |  | 0
5.2 |  | Light Points Standard. Supply, delivery and installation of fixed outlet point for light fitting, Outlets may be flush-in brick wall, cast in concrete, or surface mounted on wall or void. The rate shall be for one light point based on an average wiring distance of 10m looping from point to point. 3x2.5mm² insulated copper wire shall be used used for live, neutral and earth. Light fittings are measured elsewhere. | No | 65 |  | 0 |  | 0
5.3 |  | Light Switch Single Lever One-Way Flush Wall Mounted. Supply, deliver and installation of single lever one way light switch including cover plate and installed in flush mounted 100 x 50 mm galvanized steel box | No | 14 |  | 0 |  | 0
5.4 |  | Stove Isolator Switch Flush Wall Mounted. Supply, deliver and installation of domestic flush wall mounted stove isolator rated 60A DP. The rate shall include all wiring from the DB. 6mm2 PVC insulated copper wire shall be used for live and the neutral conductors. The rate shall further include a 60mm dia round box with cover plate and cable compression gland as well as 3m long 5 Core 6mm2 flexible cable for the connection of the stove to the isolator | No. | 2 |  | 0 |  | 0
5.5 |  | Bell Siren.Supply, delivery, and installation of School Bell / Siren with press release button. Similar or equal to SIRENCO 500SL, |  | 1 |  | 0 |  | 0
5.6 |  | Daylight Switches -Supply,delivery, installation, wiring and connection of daylight switch mounted inside a circle bulkhead light fitting over a round outlet box with a blank cover plate / or alternatively installed inside the DB - rated at 16 A, - complete - with bypass circuitbreaker. | No. | 13
5.7 |  | Commissioning of the existing installation including testing of all circuits and earthing per DB | No | 10 |  | 0 |  | 0
[6 empty] | 0 |  | 0
5.8 |  | Any other items necessary to complete the above OUTLETS AS SPECIFIED not listed elsewhere
Specify:
[6 empty] | 0 |  | 0
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 |  | 0

## Section X6
SECTION X6: ELECTRICAL INSTALLATION: LUMINAIRES
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
6 |  | LUMINAIRES
6.1 |  | Complete installed including lamps and switchgear as per schedule.
6.1.1 |  | Type 1: 2x58W T8 FLUORESCENT TUBE. Ref: MEGATECH/SKU: JC20003 | No. | 50 |  | 0 |  | 0
6.1.2 |  | Type 2: BULKHEAD WITH LED BULB Ref: MEGATECH/SKU:LA10248 | No | 15 |  | 0 |  | 0
6.2 |  | Any other items necessary to complete the above Luminaires not listed elsewhere
Specify:
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 |  | 0

## Section X7
SECTION X7: ELECTRICAL INSTALLATION: EARTHING AND LIGHTNING PROTECTION
ITEM NO | PAY-MENT CLAUSE | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR
[5 empty] | RATE | TOTAL | RATE | TOTAL
[5 empty] | N$ | N$ | N$ | N$
7 |  | EARTHING AND LIGHTNING PROTECTION
7.1 |  | Lightning protection earthing installation. Earthing of diagonally opposite metallic roof corners with 16sqmm green PVC insulated copper conductor terminating on a 1.2m long 16mm dia. solid steel copper bonded earth spike burried 1.5m below ground level: | No | 26 |  | 0 |  | 0
7.2 |  | Building Earthing and Bonding. Provide Earthing and Bonding of all metal structures and metal water pipes of the building as as well as bonding of all warm and cold water pipes at electric water heaters | Sum | 1 |  | 0 |  | 0
7.3 |  | Any other items necessary to complete the above EARTHING AND LIGHTNING PROTECTION INSTALLATION not listed elsewhere
Specify:
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 |  | 0

## Summary
SUMMARY OF BILL OF QUANTITIES
Section | Page | Description | Amount (N$)
X1 |  | PRELIMINARY AND GENERAL(Material AND Labour) | 0
X2 |  | LV CABLES AND TERMINATIONS(Material) | 0
X2 |  | LV CABLES AND TERMINATIONS(Labour) | 0
X3 |  | TRENCHES,SLEEVE PIPES AND MANHOLES(Material) | 0
X3 |  | TRENCHES,SLEEVE PIPES AND MANHOLES (Labour) | 0
X4 |  | LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR(Material) | 0
X4 |  | LV DISTRIBUTION BOARDS COMPLETE WITH SWITCHGEAR(Labour) | 0
X5 |  | OUTLETS AS SPECIFIED (Material) | 0
X5 |  | OUTLETS AS SPECIFIED(Labour) | 0
X6 |  | LUMINAIRES (Material) | 0
X6 |  | LUMINAIRES(Labour) | 0
X7 |  | EARTHING AND LIGHTNING PROTECTION(Material) | 0
X7 |  | EARTHING AND LIGHTNING PROTECTION(Labour) | 0
SUBTOTAL |  |  | 0
ADD CONTINGENCIES (10%) |  |  | 0
SUBTOTAL (Including Contingencies) |  |  | 0
ADD 15 % VAT |  |  | 0
TOTAL TO BID SUBMISSION FORM* |  |  | 0
Note: All prices in the BoQ to exclude VAT but include Import Duties if applicable
Amount in Words:
*Carry the total amount forward to Bid Submission Form
Signature of Bidder |  |  | Date