## 1. P&G
MINISTRY OF MINES & ENERGY
OSHIKOTO RURAL ELEC 2023-2024: OSHIKOTO REGION
ELECTRICAL INSTALLATIONS
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
1 | PRELIMINARY AND GENERAL
Tenderers shall allow for the following items whatever cost they may consider necessary for carrying out and observance of the item:
1.1 | Transport | Sum | 1
1.2 | Site Establishment | Sum | 1
1.3 | Setting out of Works | Sum | 1
1.4 | Progress Meetings | Sum | 1
1.5 | Attendance for measurement | Sum | 1
1.6 | Site Supervision | Sum | 1
1.7 | Insurance, Warranties | Sum | 1
1.8 | Telephone, stationery etc. | Sum | 1
1.9 | Submission of As-built drawings at completion in A3 Format | Sum | 1
1.10 | Provide 3 Sets of operation and maintenance manuals | Sum | 1
1.11 | Tests and commission entire electrical installation prior to completion. | Sum | 1
TOTAL CARRIED FORWARD TO SUMMARY

## 2. ONDJAMBAYONGHALU PS
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
2 | ONDJAMBAYONGHALU PRIMARY SCHOOL
CIVIL WORK
2.1 | Trench in pickable material for 600/1000V LT underground cables, complete with warning tape, backfill and compaction. | m | 620
2.2 | 50mm diameter PVC sleeves for cable entry installed complete including draw-wires. | m | 10
2.3 | 50mm diameter PVC long radius bends for cable entry to DB's. | No | 1
Supply and installation of channel
2.4 | - P2000 | m | 10
2.5 | - P9000 | m | 1
2.7 | Allow for making good to damaged floors and walls | Sum | 1
1000V CABLE RETICULATION
Supply and delivery and installation of 1000V PVC SWA PVC cables (copper).
2.8 | a) 16mm² x 4C (to School MeterBoard) | m | 90
2.9 | b) 10mm x 2C (Brick Classroom, Clinic, Church) | m | 430
2.10 | c) 6mm² x 2C (Ablution + Zinc Classroom) | m | 100
Supply and delivery and installation of bare copper earth wire.
2.11 | a) 10mm² | m | 90
2.12 | a) 6mm² | m | 430
2.13 | a) 4mm² | m | 100
Supply and delivery and installation of termination units including mechanical clamps, lugs, corrotion, proof bolts, nuts washers etc. to terminate the following cables:-
2.14 | a) 16mm² x 4C | No | 2
2.15 | b) 10mm x 2C | No | 14
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
2.16 | c) 6mm² x 2C | No | 6
2.16 | Allow for payment to NORED for connection fee | Sum | 1
2.17 | Supply and insall siren in metal cage | No | 1
Supply and installation of surface weatherproof lockable Meterboard including wiring and termination
2.18 | a) Enclosure with 50% spare space | No | 1
2.19 | b) 60A/TP/CB | No | 1
2.20 | b) 40A/DP/CB | No | 1
2.21 | c) 25A/SP/CB | No | 6
2.22 | d) 20A/SP/CB | No | 1
CLASSROOM BLOCKS (BRICK & ZINC)
Supply and installation of surface distribution boards complete with switchgear, doors, cables, locks.
2.23 | a) Enclosure with 20% spare space | No | 8
2.24 | b) 40A DP CB | No | 2
2.25 | c) 60A DP EL-Isolator, 6kA | No | 8
2.26 | d) 5A to 40A SP CB 6kA sockets | No | 32
2.27 | e) 10A SP MCB - 6kA - lights | No | 16
2.28 | f) 16A Isolator, by-pass | No | 2
2.29 | g) 20A TP Contactor | No | 8
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
2.30 | a) 16A SSO | No | 17
Supply, delivery and installation of the following light fittings and bulbs:-
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
2.31 | a) Type A | No | 40
2.32 | b) Type B | No | 20
2.33 | c) Type E | No | 22
2.34 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 82
2.35 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 10
2.36 | Supply and installation of earth conductor connections as required to distribution board and bonding as required. | No | 10
Supply and installation of height switches:-
2.37 | a) one way | No | 16
2.38 | b) daylight switch in bulkhead fitting | No | 2
TOILET BLOCK
Supply and installation of surface distribution boards complete with switchgear, doors, cables, locks.
2.39 | a) Enclosure weatherproof with 20% spare space | No | 1
2.40 | b) 30A DP-Isolator, 6kA | No | 1
2.41 | c) 16A SP MCB - 6kA | No | 1
2.42 | d) 16A SP Isolator, by-pass | No | 1
2.43 | e) 20A TP Contactor | No | 1
Supply, delivery and installation of the following light fittings:-
2.44 | a) E | No | 7
2.45 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 7
2.46 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
2.47 | Supply and installation of earth conductor connections as required to distribution board and bonding as required. | Sum | 1
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
Supply and installation of light switches:-
2.48 | a) one way surface weatherproof | No | 1
2.49 | b) daylight switch in bulkhead fitting | No | 1
CHURCH
2.50 | Supply and installation of readyboard with baseplate, complete | No | 1
2.51 | Supply and installation of prepaid meter with baseplate, complete | No | 1
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
2.52 | a) 16A SSO | No | 1
Supply, delivery and installation of the following light fittings:-
2.53 | a) Type A | No | 2
2.54 | b) Type E | No | 1
2.55 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 3
2.56 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
2.57 | Supply and installation of earth conductor connections as required to distribution board and bonding as required | Sum | 1
Supply and installation of light switches:-
2.58 | a) one way | No | 1
CLINIC
2.59 | Supply and installation of readyboard with baseplate, complete | No | 1
2.60 | Supply and installation of prepaid meter with baseplate, complete | No | 1
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
2.61 | a) 16A SSO | No | 1
Supply, delivery and installation of the following light fittings:-
2.62 | a) Type A | No | 2
2.63 | b) Type E | No | 1
2.64 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 3
2.65 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
2.66 | Supply and installation of earth conductor connections as required to distribution board and bonding as required | Sum | 1
Supply and installation of light switches:-
2.67 | a) one way | No | 1
TOTAL CARRIED FORWARD TO SUMMARY

## 3. ONALUTHIPA PS
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
3 | ONALUTHIPA PRIMARY SCHOOL
CIVIL WORK
3.1 | Trench in pickable material for 600/1000V LT underground cables, complete with warning tape, backfill and compaction. | m | 630
3.2 | 50mm diameter PVC sleeves for cable entry installed complete including draw-wires. | m | 10
3.3 | 50mm diameter PVC long radius bends for cable entry to DB's. | No | 1
Supply and installation of channel
3.4 | - P2000 | m | 10
3.5 | - P9000 | m | 1
3.6 | Allow for making good to damaged floors and walls | Sum | 1
1000V CABLE RETICULATION
Supply and delivery and installation of 1000V PVC SWA PVC cables (copper).
3.7 | a) 16mm² x 4C (to School MeterBoard) | m | 100
3.8 | b) 10mm x 2C (Brick Classroom, Clinic, Church) | m | 480
3.9 | c) 6mm² x 2C (Ablution + Zinc Classroom) | m | 50
Supply and delivery and installation of bare copper earth wire.
3.10 | a) 10mm² | m | 100
3.11 | a) 6mm² | m | 480
3.12 | a) 4mm² | m | 50
Supply and delivery and installation of termination units including mechanical clamps, lugs, corrotion, proof bolts, nuts washers etc. to terminate the following cables:-
3.13 | a) 16mm² x 4C | No | 2
3.14 | b) 10mm x 2C | No | 20
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
3.15 | c) 6mm² x 2C | No | 4
3.16 | Allow for payment to NORED for connection fee | Sum | 1
3.17 | Supply and insall siren in metal cage | No | 1
Supply and installation of surface weatherproof lockable Meterboard including wiring and termination
3.18 | a) Enclosure with 50% spare space | No | 1
3.19 | b) 60A/TP/CB | No | 1
3.20 | b) 40A/DP/CB | No | 1
3.21 | c) 25A/SP/CB | No | 6
3.22 | d) 20A/SP/CB | No | 1
CLASSROOM BLOCKS (BRICK & ZINC)
Supply and installation of surface distribution boards complete with switchgear, doors, cables, locks.
3.23 | a) Enclosure with 20% spare space | No | 9
3.24 | b) 40A DP CB | No | 3
3.25 | c) 60A DP EL-Isolator, 6kA | No | 9
3.26 | d) 5A to 40A SP CB 6kA sockets | No | 36
3.27 | e) 10A SP MCB - 6kA - lights | No | 18
3.28 | f) 16A Isolator, by-pass | No | 3
3.29 | g) 20A TP Contactor | No | 9
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
3.30 | a) 16A SSO | No | 13
Supply, delivery and installation of the following light fittings:-
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
3.31 | a) Type A | No | 36
3.32 | b) Type B | No | 16
3.33 | c) Type E | No | 20
3.34 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 72
3.35 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 10
3.36 | Supply and installation of earth conductor connections as required to distribution board and bonding as required. | No | 10
Supply and installation of height switches:-
3.37 | a) one way | No | 11
3.38 | b) daylight switch in bulkhead fitting | No | 3
TOILET BLOCK
Supply and installation of surface distribution boards complete with switchgear, doors, cables, locks.
3.39 | a) Enclosure weatherproof with 20% spare space | No | 1
3.40 | b) 30A DP-Isolator, 6kA | No | 1
3.41 | c) 16A SP MCB - 6kA | No | 2
3.42 | d) 16A SP Isolator, by-pass | No | 1
3.43 | e) 20A TP Contactor | No | 1
Supply, delivery and installation of the following light fittings:-
3.44 | a) E | No | 7
3.45 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 7
3.46 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 1
3.47 | Supply and installation of earth conductor connections as required to distribution board and bonding as required. | Sum | 1
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
Supply and installation of light switches:-
3.48 | a) one way surface weatherproof | No | 1
3.49 | b) daylight switch in bulkhead fitting | No | 1
CHURCH
3.50 | Supply and installation of readyboard with baseplate, complete | No | 1
3.51 | Supply and installation of prepaid meter with baseplate, complete | No | 1
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
3.52 | a) 16A SSO | No | 1
Supply, delivery and installation of the following light fittings:-
3.53 | a) Type A | No | 2
3.54 | b) Type E | No | 1
3.55 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 3
3.56 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
3.57 | Supply and installation of earth conductor connections as required to distribution board and bonding as required | Sum | 1
Supply and installation of light switches:-
3.58 | a) one way | No | 1
CLINIC
3.59 | Supply and installation of readyboard with baseplate, complete | No | 1
3.60 | Supply and installation of prepaid meter with baseplate, complete | No | 1
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
3.61 | a) 16A SSO | No | 1
Supply, delivery and installation of the following light fittings:-
3.62 | a) Type A | No | 2
3.63 | b) Type E | No | 1
3.64 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 3
3.65 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
3.66 | Supply and installation of earth conductor connections as required to distribution board and bonding as required | Sum | 1
Supply and installation of light switches:-
3.67 | a) one way | No | 1
TOTAL CARRIED FORWARD TO SUMMARY

## 4. ONANGOBE PPS
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
4 | ONANGOBE PRE-PRIMARY SCHOOL
CIVIL WORK
4.1 | Trench in pickable material for 600/1000V LT underground cables, complete with warning tape, backfill and compaction. | m | 200
4.2 | 50mm diameter PVC sleeves for cable entry installed complete including draw-wires. | m | 10
4.3 | 50mm diameter PVC long radius bends for cable entry to DB's. | No | 1
Supply and installation of channel
4.4 | - P2000 | m | 10
4.5 | - P9000 | m | 1
4.6 | Allow for making good to damaged floors and walls | Sum | 1
1000V CABLE RETICULATION
Supply and delivery and installation of 1000V PVC SWA PVC cables (copper).
4.7 | a) 16mm² x 4C (to School MeterBoard) | m | 35
4.8 | b) 10mm x 2C (Brick Classroom, Clinic, Church) | m | 160
4.9 | c) 6mm² x 2C (Ablution + Zinc Classroom) | m | 100
Supply and delivery and installation of bare copper earth wire.
4.10 | a) 10mm² | m | 35
4.11 | a) 6mm² | m | 160
4.12 | a) 4mm² | m | 100
Supply and delivery and installation of termination units including mechanical clamps, lugs, corrotion, proof bolts, nuts washers etc. to terminate the following cables:-
4.13 | a) 16mm² x 4C | No | 2
4.14 | b) 10mm x 2C | No | 6
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
4.15 | c) 6mm² x 2C | No | 6
4.16 | Allow for payment to NORED for connection fee | Sum | 1
4.17 | Supply and insall siren in metal cage | No | 1
Supply and installation of surface weatherproof lockable Meterboard including wiring and termination
4.18 | a) Enclosure with 50% spare space | No | 1
4.19 | b) 60A/TP/CB | No | 1
4.20 | b) 40A/DP/CB | No | 1
4.21 | c) 25A/SP/CB | No | 2
4.22 | d) 20A/SP/CB | No | 1
CLASSROOM BLOCKS (BRICK & ZINC)
Supply and installation of surface distribution boards complete with switchgear, doors, cables, locks.
4.23 | a) Enclosure with 20% spare space | No | 1
4.24 | b) 40A DP CB | No | 1
4.25 | c) 60A DP EL-Isolator, 6kA | No | 1
4.26 | d) 5A to 40A SP CB 6kA sockets | No | 4
4.27 | e) 10A SP MCB - 6kA - lights | No | 2
4.28 | f) 16A Isolator, by-pass | No | 2
4.29 | g) 20A TP Contactor | No | 2
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
4.30 | a) 16A SSO | No | 2
Supply, delivery and installation of the following light fittings:-
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
4.31 | a) Type A | No | 1
4.32 | c) Type E | No | 8
4.33 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 9
4.34 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
4.35 | Supply and installation of earth conductor connections as required to distribution board and bonding as required. | No | 2
Supply and installation of height switches:-
4.36 | a) one way | No | 1
4.37 | b) daylight switch in bulkhead fitting | No | 1
TOILET BLOCK
Supply and installation of surface distribution boards complete with switchgear, doors, cables, locks.
4.38 | a) Enclosure weatherproof with 20% spare space | No | 1
4.39 | b) 30A DP-Isolator, 6kA | No | 1
4.40 | c) 16A SP MCB - 6kA | No | 2
4.41 | d) 16A SP Isolator, by-pass | No | 1
4.42 | e) 20A TP Contactor | No | 1
Supply, delivery and installation of the following light fittings:-
4.43 | a) E | No | 1
4.44 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 1
4.45 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 1
4.46 | Supply and installation of earth conductor connections as required to distribution board and bonding as required. | Sum | 1
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
Supply and installation of light switches:-
4.47 | a) one way surface weatherproof | No | 1
4.48 | b) daylight switch in bulkhead fitting | No | 1
CHURCH
4.49 | Supply and installation of readyboard with baseplate, complete | No | 1
4.50 | Supply and installation of prepaid meter with baseplate, complete | No | 1
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
4.51 | a) 16A SSO | No | 1
Supply, delivery and installation of the following light fittings:-
4.52 | a) Type A | No | 2
4.53 | b) Type E | No | 1
4.54 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 3
4.55 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
4.56 | Supply and installation of earth conductor connections as required to distribution board and bonding as required | Sum | 1
Supply and installation of light switches:-
4.57 | a) one way | No | 1
CLINIC
4.58 | Supply and installation of readyboard with baseplate, complete | No | 1
4.59 | Supply and installation of prepaid meter with baseplate, complete | No | 1
TOTAL CARRIED FORWARD
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE
BROUGHT FORWARD
16 Amp surface wall mounted galvanised socket outlets including 4mm² wiring, steel conduits, saddles, bends, couplers, chasing etc.
4.60 | a) 16A SSO | No | 1
Supply, delivery and installation of the following light fittings:-
4.61 | a) Type A | No | 2
4.62 | b) Type E | No | 1
4.63 | Supply and installation of light points complete with 2,5mm² wiring, steel conduits etc. | No | 3
4.64 | Supply and installation of earth rods plus connection to roof steel as per detail. | No | 2
4.65 | Supply and installation of earth conductor connections as required to distribution board and bonding as required | Sum | 1
Supply and installation of light switches:-
4.66 | a) one way | No | 1
TOTAL CARRIED FORWARD TO SUMMARY

## 4. MAINTENANCE
ITEM | DESCRIPTION | UNIT | QTY | LABOUR RATE | MATERIAL RATE | TOTAL RATE | AMOUNT N$
5 | MAINTENANCE
5.1 | Cost required for the 12 month maintenance period including at least one site visit every 4 months. | Sum | 1 |  |  |  | 20000
TOTAL CARRIED FORWARD TO SUMMARY

## SUMMARY
SUMMARY OF SECTIONS
SECTION | DESCRIPTION
1 | PRELIMINARY AND GENERAL
2 | ONDJAMBAYONGHALU PRIMARY SCHOOL
3 | ONALUTHIPA PRIMARY SCHOOL
4 | ONANGOBE PRE-PRIMARY SCHOOL
5 | MAINTENANCE
SUB-TOTAL 1
ADD 10% CONTINGENCY
SUB-TOTAL 2
ADD 15% VAT
TOTAL CARRIED FORWARD TO FORM OF TENDER